## Modbus Registers
History
V1.6 | Marked in red changes from V1.3 to V1.5
V1.5 | Updated some Remarks
V1.4 | Updated MRS-485 status
V1.3 | Last sent ro Field Server
Location F - Flash E - EEPROM R - RAM |  | Sensor | Parameter Name | Parameter Type | Access | BRS485 Register number | Parameter Length MRS485 | Parameter Length MRS485 | Remark | BRS-485 | Registration Failed | CM-6 | GD-6 | TX-6 NH3 | TX-6 NO2 | TX-6 H2S | TX6 OX | TX6 RD | TX6 CD | CD-6H | CD-6G
[6 empty] | Decimal | Register | Bytes
F |  | Sensor 1 | S1 Memory map version | unsigned int | R | 1 | 1 | 2 |  | 1
F | MRS-485 data | Sensor 1 | S1 ProductName | ASCII String | R | 30 | 4 | 8 |  | "BRS-485"
F | Sensor fixed data | Sensor 1 | S1 Sensor Id type & Gas Id type | unsigned int | R | 34 | 1 | 2 | b7 to b0 is Sensor Id type - Read at power up on current loop during registration procedure. b15 to b8 is Gas Id type - NOT USED at this time (reads 0) |  | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
F | Sensor fixed data | Sensor 1 | S1 Sensor exponent & Sensor resolution | unsigned int | R | 35 | 1 | 2 | b7 to b0 is Sensor exponent - It is a number between -128 (0x80) and 127 (0x7f) b15 to b8 is Sensor resolution. To get sensor resolution in engineering units use the following formula: (Sensor resolution)*10^(Sensor exponent) |  | 0x1900 | 0x0100 | 0x0100 | 0x0100 | 0x01ff | 0x0100 | 0x01ff | 0x0A00 | 0x3200 | 0x3200 | 0x01FE
F | Sensor fixed data | Sensor 1 | S1 Sensor range | unsigned int | R | 36 | 1 | 2 | To get sensor range in engineering units use the following formula: (Sensor range)*10^(Sensor exponent) |  | 25000 | 200 | 50 | 100 | 200 | 50 | 250 | 990 | 2000 | 5000 | 500
R | Current loop data | Sensor 1 | S1 First current level used for current loop calibration | unsigned int | R | 74 | 1 | 2 | Current in uA
R | Current loop data | Sensor 1 | S1 Analog reading for first current level used for current loop calibration | unsigned int | R | 75 | 1 | 2 | ADC reading
R | Current loop data | Sensor 1 | S1 Second current level used for current loop calibration | unsigned int | R | 76 | 1 | 2 | Current in uA
R | Current loop data | Sensor 1 | S1 Analog reading for second current level used for current loop calibration | unsigned int | R | 77 | 1 | 2 | ADC reading
R | Sensor data | Sensor 1 | S1 Registration status | unsigned int | R | 79 | 1 | 2 | b08 - Set when no signal on current loop. b09 - Set when calibration overdue. b10 - Set when BRS-485 Status is not zero. b11 - Set during the first 60 seconds after a reset. b12 - Set when over range signal on current loop. b13 - Set when trouble signal on current loop. b14 - Set when registration is in progress. b15 - Unused Required for DVP-120M operation
R | Sensor data | Sensor 1 | S1 Reading | int | R | 80 | 1 | 2 | If registration was succesfull you get sensor reading. To get current sensor reading in engineering units use the following formula: (Current sensor reading)*10^(Sensor exponent) If registration failed you get current reading in uA
R | Sensor data | Sensor 1 | S1 Reading in float 32 bits format | float | R | 81 | 2 | 4 | Current sensor reading in float 32 bits format:
R | Sensor data | Sensor 1 | S1 BRS-485 Status | unsigned int | R | 83 | 1 | 2 | BRS-485 Status: b0 - Unused b1 - Unused b2 - Set when calibration data cannot be loaded b3 - Unused b4 - Unused b5 - Unused b6 - Unused b7 - Unused b8 - Set when unknown sensor type b9 to b14 - Unused b15 - Unused
R | For Title 24 support | Sensor 1 | S1 Registration status (same as register 79) | unsigned int | R | 91 | 1 | 2 | b08 - Set when no signal on current loop. b09 - Set when calibration overdue. b10 - Set when MRS-485 Status is not zero. b11 - Set during the first 60 seconds after a reset. b12 - Set when over range signal on current loop. b13 - Set when trouble signal on current loop. b14 - Set when registration is in progress. b15 - Set when a new registration was detected since last read and you must read again Sensor fixed data to be able to calculate correctly gas reading. You also need to write a value of 0x5aa5 to register 79 to clear this flag.
R | For Title 24 support | Sensor 1 | S1 Reading (same as register 80) | int | R | 92 | 1 | 2 | If registration was succesfull you get sensor reading. To get current sensor reading in engineering units use the following formula: (Current sensor reading)*10^(Sensor exponent) If registration failed you get current reading in uA
R | For Title 24 support | Sensor 1 | S1 UntilCalDue | unsigned int | R | 93 | 1 | 2 | Intervals of 3 hours until calibration overdue: 255 if calibration due feature is disabled 254 if unknown value (was not transmitted by detector yet) 253 if detector doesn't know about this information (you get this when you connect a version of the wireless detector which doesn't know about UntilCalDue) 241 if there are more than 30 days until calibration due 1 to 240 if there are up to 30 days until calibration due 0 if calibration overdue
R | For Title 24 support | Sensor 1 | S1 Sensor Id type & Gas Id type (same as register 34) | unsigned int | R | 94 |  |  | b7 to b0 is Sensor Id type - Read at power up on current loop during registration procedure. b15 to b8 is Gas Id type - NOT USED at this time (reads 0)
F | Extended sensor data | Sensor 1 | S1 Last Sensor Id type | unsigned int | R | 95 | 1 | 2
R | Extended sensor data | Sensor 1 | S1 Resolution in float 32 bits format | float | R | 96 | 2 | 4
R | Extended sensor data | Sensor 1 | S1 Range in float 32 bits format | float | R | 98 | 2 | 4
R | Extended sensor data | Sensor 1 | S1 Reading (Normalized to 0.1 scalar) | unsigned int | R | 100 | 1 | 2 | If registration fails, this is the current in uA
R | Extended sensor data | Sensor 1 | S1 Resolution (Normalized to 0.1 scalar) | unsigned int | R | 101 | 1 | 2 | If registration fails, this uses a scalar of 1
R | Extended sensor data | Sensor 1 | S1 Range (Normalized to 0.1 scalar) | unsigned int | R | 102 | 1 | 2 | If registration fails, this uses a scalar of 1
R | Extended sensor data | Sensor 1 | S1 Calibration Due Days | unsigned int | R | 103 | 1 | 2 | ICC addition Number of days until calibration overdue: 65535 if calibration due feature is disabled 65534 if unknown value (was not transmitted by detector yet) 65533 if detector doesn't know about this information (you get this when you connect a version of the wireless detector which doesn't know about UntilCalDue) 31 if there are more than 30 days until calibration due 1 to 30 if there are up to 30 days until calibration due 0 if calibration overdue
F |  | Sensor 2 | S2 Memory map version | unsigned int | R | 201 | 1 | 2 |  | 1
F | MRS-485 data | Sensor 2 | S2 ProductName | ASCII String | R | 230 | 4 | 8 |  | "BRS-485"
F | Sensor fixed data | Sensor 2 | S2 Sensor Id type & Gas Id type | unsigned int | R | 234 | 1 | 2 | b7 to b0 is Sensor Id type - Read at power up on current loop during registration procedure. b15 to b8 is Gas Id type - NOT USED at this time (reads 0) |  | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
F | Sensor fixed data | Sensor 2 | S2 Sensor exponent & Sensor resolution | unsigned int | R | 235 | 1 | 2 | b7 to b0 is Sensor exponent - It is a number between -128 (0x80) and 127 (0x7f) b15 to b8 is Sensor resolution. To get sensor resolution in engineering units use the following formula: (Sensor resolution)*10^(Sensor exponent) |  | 0x1900 | 0x0100 | 0x0100 | 0x0100 | 0x01ff | 0x0100 | 0x01ff | 0x0A00 | 0x3200 | 0x3200 | 0x01FE
F | Sensor fixed data | Sensor 2 | S2 Sensor range | unsigned int | R | 236 | 1 | 2 | To get sensor range in engineering units use the following formula: (Sensor range)*10^(Sensor exponent) |  | 25000 | 200 | 50 | 100 | 200 | 50 | 250 | 990 | 2000 | 5000 | 500
R | Current loop data | Sensor 2 | S2 First current level used for current loop calibration | unsigned int | R | 274 | 1 | 2 | Current in uA
R | Current loop data | Sensor 2 | S2 Analog reading for first current level used for current loop calibration | unsigned int | R | 275 | 1 | 2 | ADC reading
R | Current loop data | Sensor 2 | S2 Second current level used for current loop calibration | unsigned int | R | 276 | 1 | 2 | Current in uA
R | Current loop data | Sensor 2 | S2 Analog reading for second current level used for current loop calibration | unsigned int | R | 277 | 1 | 2 | ADC reading
R | Sensor data | Sensor 2 | S2 Registration status | unsigned int | R | 279 | 1 | 2 | b08 - Set when no signal on current loop. b09 - Set when calibration overdue. b10 - Set when BRS-485 Status is not zero. b11 - Set during the first 60 seconds after a reset. b12 - Set when over range signal on current loop. b13 - Set when trouble signal on current loop. b14 - Set when registration is in progress. b15 - Unused
R | Sensor data | Sensor 2 | S2 Reading | int | R | 280 | 1 | 2 | If registration was succesfull you get sensor reading. To get current sensor reading in engineering units use the following formula: (Current sensor reading)*10^(Sensor exponent) If registration failed you get current reading in uA
R | Sensor data | Sensor 2 | S2 Reading in float 32 bits format | float | R | 281 | 2 | 4 | Current sensor reading in float 32 bits format:
R | Sensor data | Sensor 2 | S2 BRS-485 Status | unsigned int | R | 283 | 1 | 2 | BRS-485 Status: b0 - Unused b1 - Unused b2 - Set when calibration data cannot be loaded b3 - Unused b4 - Unused b5 - Unused b6 - Unused b7 - Unused b8 - Set when unknown sensor type b9 to b14 - Unused b15 - Unused
R | For Title 24 support | Sensor 2 | S2 Registration status (same as register 279) | unsigned int | R | 291 | 1 | 2 | b08 - Set when no signal on current loop. b09 - Set when calibration overdue. b10 - Set when MRS-485 Status is not zero. b11 - Set during the first 60 seconds after a reset. b12 - Set when over range signal on current loop. b13 - Set when trouble signal on current loop. b14 - Set when registration is in progress. b15 - Set when a new registration was detected since last read and you must read again Sensor fixed data to be able to calculate correctly gas reading. You also need to write a value of 0x5aa5 to register 79 to clear this flag.
R | For Title 24 support | Sensor 2 | S2 Reading (same as register 280) | int | R | 292 | 1 | 2 | If registration was succesfull you get sensor reading. To get current sensor reading in engineering units use the following formula: (Current sensor reading)*10^(Sensor exponent) If registration failed you get current reading in uA
R | For Title 24 support | Sensor 2 | S2 UntilCalDue | unsigned int | R | 293 | 1 | 2 | Intervals of 3 hours until calibration overdue: 255 if calibration due feature is disabled 254 if unknown value (was not transmitted by detector yet) 253 if detector doesn't know about this information (you get this when you connect a version of the wireless detector which doesn't know about UntilCalDue) 241 if there are more than 30 days until calibration due 1 to 240 if there are up to 30 days until calibration due 0 if calibration overdue
R | For Title 24 support | Sensor 2 | S2 Sensor Id type & Gas Id type (same as register 234) | unsigned int | R | 294 |  |  | b7 to b0 is Sensor Id type - Read at power up on current loop during registration procedure. b15 to b8 is Gas Id type - NOT USED at this time (reads 0)
F | Extended sensor data | Sensor 2 | S2 Last Sensor Id type | unsigned int | R | 295 | 1 | 2
R | Extended sensor data | Sensor 2 | S2 Resolution in float 32 bits format | float | R | 296 | 2 | 4
R | Extended sensor data | Sensor 2 | S2 Range in float 32 bits format | float | R | 298 | 2 | 4
R | Extended sensor data | Sensor 2 | S2 Reading (Normalized to 0.1 scalar) | unsigned int | R | 300 | 1 | 2 | If registration fails, this is the current in uA
R | Extended sensor data | Sensor 2 | S2 Resolution (Normalized to 0.1 scalar) | unsigned int | R | 301 | 1 | 2 | If registration fails, this uses a scalar of 1
R | Extended sensor data | Sensor 2 | S2 Range (Normalized to 0.1 scalar) | unsigned int | R | 302 | 1 | 2 | If registration fails, this uses a scalar of 1
R | Extended sensor data | Sensor 2 | S2 Calibration Due Days | unsigned int | R | 303 | 1 | 2 | Number of days until calibration overdue: 65535 if calibration due feature is disabled 65534 if unknown value (was not transmitted by detector yet) 65533 if detector doesn't know about this information (you get this when you connect a version of the wireless detector which doesn't know about UntilCalDue) 31 if there are more than 30 days until calibration due 1 to 30 if there are up to 30 days until calibration due 0 if calibration overdue

## BACnet Objects
Sensor | Object Type | Object Instance | Object Name | Units | Default COV Increment | Active Text | Inactive Text | Relinquish Default | Remark | Registration Failed | CM-6 | GD-6 | TX-6 NH3 | TX-6 NO2 | TX-6 H2S | TX6 OX | TX6 RD | TX6 CD | CD-6H | CD-6G
Sensor 1 | Analog Input | 1 | S1 Snsr Reading | No Units | 2 | N/A | N/A | N/A | Current sensor reading in float 32 bits format
Sensor 1 | Analog Value | 1 | S1 Sensor Type | No Units | 0 | N/A | N/A | 0 | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 1 | Analog Value | 2 | S1 Resolution | No Units | 0 | N/A | N/A | 0 | Sensor resolution in float 32 bits format | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 1 | Analog Value | 3 | S1 Range | No Units | 0 | N/A | N/A | 0 | Sensor range in float 32 bits format | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 1 | Analog Value | 4 | S1 Last Sns Type | No Units | 0 | N/A | N/A | 0 | Sensor ID type detected at last power on
Sensor 1 | Analog Value | 5 | S1 Cal Due Days | No Units | 0 | N/A | N/A | 0 | Number of days until calibration overdue
Sensor 1 | Analog Value | 6 | S1 UntilCalDue | No Units | 0 | N/A | N/A | 0 | Intervals of 3 hours until calibration overdue
Sensor 1 | Binary Value | 1 | S1 No Signal | N/A | N/A | Error | OK | Inactive | Set when no signal on current loop.
Sensor 1 | Binary Value | 2 | S1 Cal Overdue | N/A | N/A | Error | OK | Inactive | Set when calibration overdue.
Sensor 1 | Binary Value | 3 | S1 BRS485 Status | N/A | N/A | Error | OK | Inactive | Set when BRS-485 Status is not zero.
Sensor 1 | Binary Value | 4 | S1 Warmup | N/A | N/A | Warmup | Ready | Inactive | Set during the first 60 seconds after a reset.
Sensor 1 | Binary Value | 5 | S1 Over Range | N/A | N/A | Error | OK | Inactive | Set when over range signal on current loop.
Sensor 1 | Binary Value | 6 | S1 Trouble | N/A | N/A | Error | OK | Inactive | Set when trouble signal on current loop.
Sensor 1 | Binary Value | 7 | S1 Cal Error | N/A | N/A | Error | OK | Inactive | Set when calibration data cannot be loaded
Sensor 1 | Binary Value | 8 | S1 Unknown Snsr | N/A | N/A | Error | OK | Inactive | Set when unknown sensor type
Sensor 2 | Analog Input | 21 | S2 Snsr Reading | No Units | 2 | N/A | N/A | N/A | Current sensor reading in float 32 bits format
Sensor 2 | Analog Value | 21 | S2 Sensor Type | No Units | 0 | N/A | N/A | 0 | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 2 | Analog Value | 22 | S2 Resolution | No Units | 0 | N/A | N/A | 0 | Sensor resolution in float 32 bits format | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 2 | Analog Value | 23 | S2 Range | No Units | 0 | N/A | N/A | 0 | Sensor range in float 32 bits format | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 2 | Analog Value | 24 | S2 Last Sns Type | No Units | 0 | N/A | N/A | 0 | Sensor ID type detected at last power on
Sensor 2 | Analog Value | 25 | S2 Cal Due Days | No Units | 0 | N/A | N/A | 0 | Number of days until calibration overdue
Sensor 2 | Analog Value | 26 | S2 UntilCalDue | No Units | 0 | N/A | N/A | 0 | Intervals of 3 hours until calibration overdue
Sensor 2 | Binary Value | 21 | S2 No Signal | N/A | N/A | Error | OK | Inactive | Set when no signal on current loop.
Sensor 2 | Binary Value | 22 | S2 Cal Overdue | N/A | N/A | Error | OK | Inactive | Set when calibration overdue.
Sensor 2 | Binary Value | 23 | S2 BRS485 Status | N/A | N/A | Error | OK | Inactive | Set when BRS-485 Status is not zero.
Sensor 2 | Binary Value | 24 | S2 Warmup | N/A | N/A | Warmup | Ready | Inactive | Set during the first 60 seconds after a reset.
Sensor 2 | Binary Value | 25 | S2 Over Range | N/A | N/A | Error | OK | Inactive | Set when over range signal on current loop.
Sensor 2 | Binary Value | 26 | S2 Trouble | N/A | N/A | Error | OK | Inactive | Set when trouble signal on current loop.
Sensor 2 | Binary Value | 27 | S2 Cal Error | N/A | N/A | Error | OK | Inactive | Set when calibration data cannot be loaded
Sensor 2 | Binary Value | 28 | S2 Unknown Snsr | N/A | N/A | Error | OK | Inactive | Set when unknown sensor type

## Metasys N2 Objects
Sensor | Object Type | Object Instance | Object Name | Remark | Registration Failed | CM-6 | GD-6 | TX-6 NH3 | TX-6 NO2 | TX-6 H2S | TX6 OX | TX6 RD | TX6 CD | CD-6H | CD-6G
Sensor 1 | Analog Input | 1 | S1 Sensor Reading | Current sensor reading in float 32 bits format
Sensor 1 | Analog Input | 2 | S1 Sensor Type | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 1 | Analog Input | 3 | S1 Resolution | Sensor resolution in float 32 bits format | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 1 | Analog Input | 4 | S1 Range | Sensor range in float 32 bits format | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 1 | Analog Input | 5 | S1 Last Sensor Type | Sensor ID type detected at last power on
Sensor 1 | Analog Input | 6 | S1 Cal Due Days | Number of days until calibration overdue
Sensor 1 | Analog Input | 7 | S1 UntilCalDue | Intervals of 3 hours until calibration overdue
Sensor 1 | Binary Input | 1 | S1 No Signal | Set when no signal on current loop.
Sensor 1 | Binary Input | 2 | S1 Cal Overdue | Set when calibration overdue.
Sensor 1 | Binary Input | 3 | S1 BRS-485 Status | Set when BRS-485 Status is not zero.
Sensor 1 | Binary Input | 4 | S1 Warmup | Set during the first 60 seconds after a reset.
Sensor 1 | Binary Input | 5 | S1 Over Range | Set when over range signal on current loop.
Sensor 1 | Binary Input | 6 | S1 Trouble | Set when trouble signal on current loop.
Sensor 1 | Binary Input | 7 | S1 Cal Error | Set when calibration data cannot be loaded
Sensor 1 | Binary Input | 8 | S1 Unknown Sensor | Set when unknown sensor type
Sensor 2 | Analog Input | 21 | S2 Sensor Reading | Current sensor reading in float 32 bits format
Sensor 2 | Analog Input | 22 | S2 Sensor Type | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 2 | Analog Input | 23 | S2 Resolution | Sensor resolution in float 32 bits format | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 2 | Analog Input | 24 | S2 Range | Sensor range in float 32 bits format | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 2 | Analog Input | 25 | S2 Last Sensor Type | Sensor ID type detected at last power on
Sensor 2 | Analog Input | 26 | S2 Cal Due Days | Number of days until calibration overdue
Sensor 2 | Analog Input | 27 | S2 UntilCalDue | Intervals of 3 hours until calibration overdue
Sensor 2 | Binary Input | 21 | S2 No Signal | Set when no signal on current loop.
Sensor 2 | Binary Input | 22 | S2 Cal Overdue | Set when calibration overdue.
Sensor 2 | Binary Input | 23 | S2 BRS-485 Status | Set when BRS-485 Status is not zero.
Sensor 2 | Binary Input | 24 | S2 Warmup | Set during the first 60 seconds after a reset.
Sensor 2 | Binary Input | 25 | S2 Over Range | Set when over range signal on current loop.
Sensor 2 | Binary Input | 26 | S2 Trouble | Set when trouble signal on current loop.
Sensor 2 | Binary Input | 27 | S2 Cal Error | Set when calibration data cannot be loaded
Sensor 2 | Binary Input | 28 | S2 Unknown Sensor | Set when unknown sensor type

## Siemens FLN Points
Application Number |  |  | 7362
Application Descriptor |  |  | BRS 485
Sensor | Point Type | Point Number | Point Name | Slope | Intercept | Units | On Text | Off Text | Remark | Registration Failed | CM-6 | GD-6 | TX-6 NH3 | TX-6 NO2 | TX-6 H2S | TX6 OX | TX6 RD | TX6 CD | CD-6H | CD-6G
| LAO | 1 | CTLR ADDRESS | 1 | 0 |  | N/A | N/A | FLN slave address (0 - 99)
| LAO | 2 | APPLICATION | 1 | 0 |  | N/A | N/A | 7362 Non-configurable
Sensor 1 | LAI | 3 | S1 READING | 0.1 | 0 |  | N/A | N/A | Current sensor reading
Sensor 1 | LAI | 4 | S1 SNSR TYPE | 1 | 0 |  | N/A | N/A | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 1 | LAI | 5 | S1 RESOLUTN | 0.1 | 0 |  | N/A | N/A | Sensor resolution | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 1 | LAI | 6 | S1 RANGE | 0.1 | 0 |  | N/A | N/A | Sensor range | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 1 | LAI | 7 | S1 LAST TYPE | 1 | 0 |  | N/A | N/A | Sensor ID type detected at last power on
Sensor 1 | LAI | 8 | S1 CAL DUE D | 1 | 0 |  | N/A | N/A | Number of days until calibration overdue
Sensor 1 | LAI | 9 | S1 UNTILCALD | 1 | 0 |  | N/A | N/A | Intervals of 3 hours until calibration overdue
Sensor 1 | LDI | 10 | S1 NO SIGNAL | N/A | N/A | N/A | ERROR | OK | Set when no signal on current loop.
Sensor 1 | LDI | 11 | S1 CAL OVERD | N/A | N/A | N/A | ERROR | OK | Set when calibration overdue.
Sensor 1 | LDI | 12 | S1 BRS STAT | N/A | N/A | N/A | ERROR | OK | Set when BRS-485 Status is not zero.
Sensor 1 | LDI | 13 | S1 WARMUP | N/A | N/A | N/A | WARMUP | READY | Set during the first 60 seconds after a reset.
Sensor 1 | LDI | 14 | S1 OVER RG | N/A | N/A | N/A | ERROR | OK | Set when over range signal on current loop.
Sensor 1 | LDI | 15 | S1 TROUBLE | N/A | N/A | N/A | ERROR | OK | Set when trouble signal on current loop.
Sensor 1 | LDI | 16 | S1 CAL ERROR | N/A | N/A | N/A | ERROR | OK | Set when calibration data cannot be loaded
Sensor 1 | LDI | 17 | S1 UNKN SNSR | N/A | N/A | N/A | ERROR | OK | Set when unknown sensor type
| LAO | 20 | OVRD TIME | 1 | 0 | HRS | N/A | N/A | These are mandatory FLN points required for compatibility with Siemens control systems. They have no effect in this application.
| LDO | 29 | DAY.NGT | N/A | N/A | N/A | NIGHT | DAY
Sensor 2 | LAI | 33 | S2 READING | 0.1 | 0 |  | N/A | N/A | Current sensor reading
Sensor 2 | LAI | 34 | S2 SNSR TYPE | 1 | 0 |  | N/A | N/A | Sensor Id type - Read at power up on current loop during registration procedure. | 0 | 1 | 3 | 4 | 2 | 5 | 8 | 6 | 7 | 9 | 10
Sensor 2 | LAI | 35 | S2 RESOLUTN | 0.1 | 0 |  | N/A | N/A | Sensor resolution | 25 | 1 | 1 | 1 | 0.1 | 1 | 0.1 | 10 | 50 | 50 | 0.01
Sensor 2 | LAI | 36 | S2 RANGE | 0.1 | 0 |  | N/A | N/A | Sensor range | 25000 | 200 | 50 | 100 | 20 | 50 | 25 | 990 | 2000 | 5000 | 5
Sensor 2 | LAI | 37 | S2 LAST TYPE | 1 | 0 |  | N/A | N/A | Sensor ID type detected at last power on
Sensor 2 | LAI | 38 | S2 CAL DUE D | 1 | 0 |  | N/A | N/A | Number of days until calibration overdue
Sensor 2 | LAI | 39 | S2 UNTILCALD | 1 | 0 |  | N/A | N/A | Intervals of 3 hours until calibration overdue
Sensor 2 | LDI | 40 | S2 NO SIGNAL | N/A | N/A | N/A | ERROR | OK | Set when no signal on current loop.
Sensor 2 | LDI | 41 | S2 CAL OVERD | N/A | N/A | N/A | ERROR | OK | Set when calibration overdue.
Sensor 2 | LDI | 42 | S2 BRS STAT | N/A | N/A | N/A | ERROR | OK | Set when BRS-485 Status is not zero.
Sensor 2 | LDI | 43 | S2 WARMUP | N/A | N/A | N/A | WARMUP | READY | Set during the first 60 seconds after a reset.
Sensor 2 | LDI | 44 | S2 OVER RG | N/A | N/A | N/A | ERROR | OK | Set when over range signal on current loop.
Sensor 2 | LDI | 45 | S2 TROUBLE | N/A | N/A | N/A | ERROR | OK | Set when trouble signal on current loop.
Sensor 2 | LDI | 46 | S2 CAL ERROR | N/A | N/A | N/A | ERROR | OK | Set when calibration data cannot be loaded
Sensor 2 | LDI | 47 | S2 UNKN SNSR | N/A | N/A | N/A | ERROR | OK | Set when unknown sensor type
| LAO | 99 | ERROR STATUS | 1 | 0 |  | N | N/A | This is a mandatory FLN point required for compatibility with Siemens control systems. It has no effect in this application.